## Sayfa1
Fill |  | cells
General |  |  | Core (square) |  |  | Transformer equivalent circuit parameters
vin (volt) | 3000 |  | required core area(m^2) | 0.067568
Nprimary(turn) | 20 |  | real core area (m^2) | 0.075075
B(tesla) | 1 |  | core depth(m) | 0.274
f(hz) | 500
Nsecondary turn | 2000
|  |  | Stacking factor | 0.9
primary cable dimensions (mm) AxB | 27 | 27 | Core loss at 1 teslaW/kg | 7.5
secondary cable dimensions (mm) AxB | 2.9 | 2.9 | loss coefficient W/kg | 7.5
Insulation per layer hV (mm) | 1.5
Insulation per layer LV (mm) | 0.5
Windings
Primary turns per layer | 10
Secondary turns per layer | 80 |  | gap height(mm) | 300
primary layers | 2 |  | gap lenght(mm) | 215
secondary layers | 25 |  | Core height(mm) | 847.9966
Hprimary winding (mm) | 270 |  | Core lenght(mm) | 762.9966
Hsecondary winding(mm) | 232 |  | Core volume(cm^3) | 143648.1925
Lprimary(mm) | 55 |  | Core density (gr/cm^3) | 7.65
Lsecondary(mm) | 110 |  | Core weight (kg) | 1098.9087
|  |  | Core Loss kW | 8.2418
|  |  | Copper Loss kW | 10.3255 | at full load
Ravg primary winding (mm) | 221.2461
Ravg secondary winding (mm) | 248.7461 |  | Total Loss kW | 18.5673
L primary (m) | 29.7885 |  | Efficiency | 0.99715
Lsecondary (m) | 3126.2506
Resistivity heat coefficient | 1.3
R per meter primary ohm/m | 3.4944e-05
R per metersecondary ohm/m | 0.0034944
Rprimary | 0.0010409
Rsecondary | 10.9244
Loss primary | 5038.099
Loss secondary | 5287.3951